## Table 1
2022 Blazer Water Treatment Plant Summary
Blazer Treated Water (Entering the Distribution System)
| Parameter | Units | Winter (Feb 2022) | Summer (Aug 2022) | Average | Guideline | Common Source
| Aluminum | mg/L | 0.0735 | 0.202 | 0.13775 | < 0.100 OG Annual Avg. | Naturally occurring and plant treatment process chemicals
| Ammonia | mg/L as N | 0.0064 | <0.0050 | <0.0057 | No Maximum | Naturally occurring; released agricultural or industrial wastes
| Antimony | mg/L | <0.00010 | <0.00010 | <0.00010 | 0.006 MAC | Erosion of natural deposits in watershed
| Arsenic | mg/L | 0.00014 | 0.00018 | 0.00016 | 0.01 ALARA | Erosion of natural deposits in watershed
| Atrazine + metabolites | mg/L | <0.00020 | <0.00020 | <0.00020 | 0.005 MAC | Leaching and/or runoff from agricultural use
| Barium | mg/L | 0.036 | 0.0295 | 0.03275 | 2 MAC | Erosion of natural deposits in watershed
| Benzene | mg/L | <0.00050 | <0.00050 | <0.00050 | 0.005 MAC | Releases or spills from industrial use
| Benzo(a)pyrene | mg/L | <0.0000050 | <0.0000050 | <0.0000050 | 0.00004 MAC | Distribution system materials
| Boron | mg/L | <0.010 | <0.010 | <0.010 | 5 MAC | Naturally occurring; leaching or runoff from industrial use
| Bromate | mg/L | <0.00030 | 0.00072 | <0.00051 | 0.01 MAC | Possible contamination in hypochlorite solution
| Bromoxynil | mg/L | <0.000050 | <0.000050 | <0.000050 | 0.005 MAC | Leaching and/or runoff from agricultural use
| Cadmium | mg/L | <0.0000050 | <0.0000050 | <0.0000050 | 0.007 MAC | Erosion of natural deposits in watershed
| Calcium | mg/L | 47 | 34.8 | 40.9 | No Maximum | Erosion of natural deposits in watershed
| Carbon Tetrachloride | mg/L | <0.00050 | <0.00050 | <0.00050 | 0.002 MAC | Industrial effluents and leaching from hazardous waste sites
| Chloramines | mg/L | 0.3 | 0.2 | 0.25 | No Maximum | Formed in the presence of both chlorine and ammonia
| Chloride | mg/L | 6.91 | 4.52 | 5.715 | ≤250 AO | Naturally occurring, dissolved salt deposits, highway salt
| Chlorpyrifos | mg/L | <0.00010 | <0.00010 | <0.00010 | 0.09 MAC | Leaching and/or runoff from agricultural use
| Chromium | mg/L | <0.00050 | <0.00050 | <0.00050 | 0.05 MAC | Erosion of natural deposits in watershed
| Colour | TCU | <5.0 | <5.0 | <5.0 | 15 AO | Erosion of natural deposits in watershed
| Coliforms, E.Coli | PA/100mL | Absent | Absent | Absent | 0 MAC | Domestic animals, wildlife, human waste
| Coliforms, Total | PA/100mL | Absent | Absent | Absent | 0 MAC | Soil, domestic animals and wildlife
| Copper | mg/L | 0.00085 | <0.00050 | <0.00068 | 2 MAC | Erosion of natural deposits in watershed
| Cyanazine | mg/L | <0.00010 | <0.00010 | <0.00010 | No Maximum | Leaching and/or runoff from agricultural use
| Cyanide | mg/L | <0.0050 | <0.0050 | <0.0050 | 0.2 MAC | Industrial and mining effluents; Release from organic compounds.
| Cyanobacterial Toxins - As Microcystin, Total | mg/L | <0.00020 | <0.00020 | <0.00020 | 0.0015 MAC | Naturally occurring; released from blooms of blue-green algae
| Diazinon | mg/L | <0.00010 | <0.00010 | <0.00010 | 0.02 MAC | Run off from agricultural or other uses.
| Dicamba | mg/L | <0.00010 | <0.00010 | <0.00010 | 0.12 MAC | Leaching and/or runoff from agricultural use
| 1,2-Dichlorobenzene | mg/L | <0.00050 | <0.00050 | <0.00050 | 0.2 MAC | Releases or spills from industrial use
| 1,4-Dichlorobenzene | mg/L | <0.00050 | <0.00050 | <0.00050 | 0.005 MAC | Releases or spills from industrial use
| 1,2 Dichloroethane | mg/L | <0.00050 | <0.00050 | <0.00050 | 0.005 MAC | Releases or spills from industrial use
| Dichloromethane | mg/L | <0.0010 | <0.0010 | <0.0010 | 0.05 MAC | Industrial and municipal wastewater discharges
| 2,4-Dichlorophenol | mg/L | <0.00030 | <0.00030 | <0.00030 | 0.9 MAC | By-product of chlorination.
| 2,4 D (2,4-Dichlorophenoxy acetic acid) | mg/L | <0.000050 | <0.000050 | <0.000050 | 0.1 MAC | Leaching and/or runoff from use as a weed controller
| Diclofop-methyl | mg/L | <0.00010 | <0.00010 | <0.00010 | 0.009 MAC | Leaching and/or runoff from use as a weed controller
| Dimethoate | mg/L | <0.00010 | <0.00010 | <0.00010 | 0.02 MAC | Leaching and/or runoff from agricultural use
| Diuron | mg/L | <0.0010 | <0.0010 | <0.0010 | 0.15 MAC | Leaching and/or runoff from use in controlling vegetation
| Ethylbenzene | mg/L | <0.00050 | <0.00050 | <0.00050 | 0.14 MAC | Emissions, effluents or spills from petroleum and chemical industries
| Fluoride1 | mg/L | 0.14 | 0.079 | 0.1095 | 1.5 MAC | Erosion of natural deposits in watershed
| Glyphosate | mg/L | <0.00020 | <0.00020 | <0.00020 | 0.28 MAC | Leaching and/or runoff from use as a weed controller
| Haloacetic Acid, Total | mg/L | 0.00921 | 0.00911 | 0.00916 | 0.08 ALARA | By-product of chlorination
| Hardness, Total | mg/L as CaCO3 | 180 | 136 | 158 | No Maximum | Erosion of natural deposits in watershed
| Iron | mg/L | <0.010 | <0.010 | <0.010 | ≤0.300 AO | Erosion of natural deposits in watershed
| Lead | mg/L | <0.000050 | <0.000050 | <0.000050 | 0.005 ALARA | Leaching from plumbing (pipes, solder, brass fittings, lead service lines)
| Magnesium | mg/L | 15.1 | 11.9 | 13.5 | No Maximum | Erosion of natural deposits in watershed
| Malathion | mg/L | <0.00010 | <0.00010 | <0.00010 | 0.19 MAC | Leaching and/or runoff from agricultural and other uses
| Manganese | mg/L | 0.00024 | 0.00012 | 0.00018 | 0.12 MAC | Erosion of natural deposits in watershed
| Mercury | mg/L | <0.0000050 | <0.0000050 | <0.0000050 | 0.001 MAC | Erosion of natural deposits in watershed
| Methoxychlor | mg/L | <0.0000080 | <0.0000080 | <0.0000080 | No Maximum | Leaching and/or runoff from agricultural and other uses
| Metolachlor | mg/L | <0.00010 | <0.00010 | <0.00010 | 0.05 MAC | Leaching and/or runoff from agricultural and other uses
| Metribuzin | mg/L | <0.00010 | <0.00010 | <0.00010 | 0.08 MAC | Leaching and/or runoff from agricultural use
| Monochlorobenzene | mg/L | <0.00050 | <0.00050 | <0.00050 | 0.08 MAC | Releases or spills from industrial effluents
| Nitrate | mg/L as N | 0.178 | 0.087 | 0.1325 | 10 (as N) MAC | Erosion of natural deposits in watershed
| Nitrite | mg/L as N | <0.010 | <0.010 | <0.010 | 1 (as N) MAC | Erosion of natural deposits in watershed
| Nitrilotriacetic Acid (NTA) | mg/L | <0.20 | <0.20 | <0.20 | 0.40 MAC | Sewage contamination
| Pentachlorophenol | mg/L | <0.00050 | <0.00050 | <0.00050 | 0.06 MAC | By-product of chlorination
| pH | pH units | 8.32 | 8.1 | 8.21 | 7-10.5 MAC | Influenced by dissolved minerals in water, temp, and treatment process
| Picloram | mg/L | <0.00010 | <0.00010 | <0.00010 | 0.19 MAC | Leaching and/or runoff from agricultural and other uses
| Selenium | mg/L | 0.00062 | 0.00043 | 0.000525 | 0.05 MAC | Naturally occurring (erosion and weathering of rocks and soils)
| Silver | mg/L | <0.000010 | <0.000010 | <0.000010 | No Maximum | Naturally occurring (erosion and weathering of rocks and soils)
| Simazine | mg/L | <0.00010 | <0.00010 | <0.00010 | 0.01 MAC | Leaching and/or runoff from agricultural and other uses
| Sodium | mg/L | 5.57 | 3.92 | 4.745 | ≤200 AO | Erosion of natural deposits in watershed
| Sulphate (Sulfate) | mg/L | 50.8 | 31.8 | 41.3 | ≤500 AO | Erosion of natural deposits in watershed
| Sulphide as S | mg/L | <0.0015 | <0.0015 | <0.0015 | ≤0.05 AO | Reduction of sulphates by sulphate-reducing bacteria; industrial wastes
| Terbufos | mg/L | <0.00010 | <0.00010 | <0.00010 | 0.001 MAC | Leaching and/or runoff from agricultural and other uses
| Tetrachloroethylene | mg/L | <0.00050 | <0.00050 | <0.00050 | 0.01 MAC | Industrial effluents or spills
| 2,3,4,6-Tetrachorophenol | mg/L | <0.00050 | <0.00050 | <0.00050 | 0.1 MAC | By-product of chlorination; industrial effluents and use of pesticides
| Toluene | mg/L | <0.00040 | <0.00040 | <0.00040 | 0.06 MAC | Emissions, effluents or spills from petroleum and chemical industries
| Total Dissolved Solids | mg/L | 174 | 182 | 178 | 500 AO | Erosion of natural deposits in watershed
| Total Organic Carbon | mg/L | <0.50 | 0.89 | <0.70 | No Maximum | Erosion of natural deposits in watershed
| Trichloroethylene | mg/L | <0.00050 | <0.00050 | <0.00050 | 0.005 MAC | Industrial effluents and spills from improper disposals
| 2,4,6-Trichlorophenol | mg/L | <0.00050 | <0.00050 | <0.00050 | 0.005 MAC | By-product of chlorination; industrial effluents and spills
| Trifluralin | mg/L | <0.00010 | <0.00010 | <0.00010 | 0.045 MAC | Runoff from agricultural uses
| Trihalomethanes, Total | mg/L | 0.0096 | 0.0283 | 0.01895 | 0.1 MAC | By-product of chlorination
| Uranium | mg/L | 0.000505 | 0.000453 | 0.000479 | 0.02 MAC | Industrial effluents or spills
| Vinyl Chloride | mg/L | <0.00040 | <0.00040 | <0.00040 | 0.002 ALARA | Industrial effluents; degradation product from organic solvents in groundwater; leaching from PVC pipes
| Xylenes (total) | mg/L | <0.00050 | <0.00050 | <0.00050 | 0.09 MAC | Emissions, effluents or spills from petroleum and chemical industries
| Zinc | mg/L | <0.0030 | <0.0030 | <0.0030 | ≤5.000 AO | Erosion of natural deposits in watershed/leaching from plumbing fixtures
Legend
1 Fluoride is not added at the Blazer Water Treatment Plant
(AO) Aesthetic Objective as determined by Health Canada
(ALARA) As Low As Reasonably Achievable as determined by Health Canada
(OG) Operating guidance as determined by Health Canada
(MAC) Maximum Acceptable Concentration as determined by Health Canada
< Indicates not detected above the specified parameter (less than)
mg/L = milligrams per litre, or parts per million
TCU = True Colour Units
PA = Present or Absent
Links
Health Canada Guidelines for Canadian Drinking Water Quality, Summary Table (Sept 2020)
Health Canada Water Quality - Reports and Publications
Alberta Environment and Parks
Potable Water Regulation