{"text_format":"1","workbook":"xlsx","n_sheets":1,"sheets":["Prescriptive & Trade-off"],"not_rendered":{"charts":0,"images":1,"macros":1,"external_links":0,"defined_names":0,"comments":1,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Prescriptive & Trade-off","index":0,"n_rows":112,"n_cols":8,"rows_kept":112,"cut":false,"hidden":false,"merged":[[111,4,120,7],[111,0,120,3],[110,1,110,3],[110,5,110,7],[109,0,109,6],[219,0,219,7],[108,0,108,7],[94,4,94,5],[94,0,94,3],[97,0,97,7],[95,6,95,7],[96,0,96,6],[94,6,94,7],[95,4,95,5],[95,0,95,3],[106,4,107,5],[106,6,106,7],[106,0,107,3],[86,0,87,7],[84,0,84,7],[89,0,89,7],[90,0,90,7],[88,0,88,6],[91,0,91,6],[107,6,107,7],[93,0,93,3],[93,4,93,5],[93,6,93,7],[92,0,92,3],[92,4,92,5],[92,6,92,7],[105,6,105,7],[99,0,100,7],[105,0,105,3],[101,0,101,6],[104,0,104,6],[103,0,103,7],[102,0,102,7],[83,0,83,6],[105,4,105,5],[35,6,35,7],[32,0,32,4],[44,0,44,6],[42,0,42,7],[43,0,43,7],[49,0,49,6],[45,0,45,6],[36,0,36,7],[37,6,37,7],[38,6,38,7],[39,6,39,7],[48,0,48,7],[38,4,38,5],[39,4,39,5],[38,0,38,3],[39,0,39,3],[40,0,40,6],[41,0,41,6],[46,0,46,6],[47,0,47,6],[32,6,32,7],[34,6,34,7],[33,6,33,7],[21,0,21,4],[22,0,22,4],[24,0,24,4],[25,0,25,4],[23,0,23,4],[37,4,37,5],[37,0,37,3],[31,0,31,4],[35,0,35,4],[33,0,33,4],[34,0,34,4],[27,0,27,4],[28,0,28,4],[26,0,26,4],[29,0,29,4],[31,5,31,7],[30,0,30,7],[12,0,12,7],[18,0,18,7],[13,0,13,7],[16,0,16,6],[17,0,17,6],[14,0,14,6],[15,0,15,6],[19,0,20,4],[19,5,20,5],[19,6,19,7],[10,0,10,7],[11,0,11,7],[2,0,3,7],[9,0,9,7],[4,1,4,4],[5,1,5,4],[6,1,6,4],[7,1,7,4],[4,5,7,7],[73,0,73,3],[74,6,74,7],[75,6,75,7],[77,0,77,6],[78,0,78,6],[79,0,79,6],[82,0,82,6],[81,0,81,6],[80,0,80,6],[74,4,75,5],[76,0,76,6],[74,0,75,3],[60,0,60,7],[58,0,58,4],[67,0,67,6],[70,0,70,6],[68,0,68,7],[71,6,71,7],[69,0,69,7],[66,1,66,4],[71,4,71,5],[71,0,72,3],[50,0,50,6],[51,1,51,6],[52,1,52,6],[53,1,53,6],[51,0,53,0],[55,0,55,6],[59,0,59,6],[57,0,57,4],[56,0,56,7],[57,5,57,7],[58,5,58,7],[54,1,54,6]]}
[]
["Report Submission for:",null,"Building Permit Application",null,"Schedule C/Occupancy Verification"]
["Statement of Compliance - National Energy Code of Canada for Buildings 2020                                                                                 "]
[]
["Project Name:",null,null,null,null,"Building Permit Number \n(Completed Internally)"]
["Project Address:"]
["Applicant Name:"]
["Applicant Address:"]
["Please note that this Performance Compliance Summary must be accompanied by an NECB Part 8 Energy Model Report at the time of submission. The applicant can choose to submit their own report generated by energy modeling software or complete and submit the reports contained within this document. Both forms of report should include:                                           "]
[]
["         1.  All relevant information as required in NECB Division C 2.2.2.3-7 is included in drawings or supplementary submissions."]
[]
["Part 3 - Building Envelope"]
["General "]
["All prescriptive requirements in Division B, Section 3.2 met? ",null,null,null,null,null,null,"N/A"]
["All Trade-off requirements in Division B, Section 3.3 met? ",null,null,null,null,null,null,"N/A"]
["Effective thermal transmittance including the effects of thermal bridging has been calculated as per Section 3.1.1.7? ",null,null,null,null,null,null,"N/A"]
["The building envelope meets air leakage requirements from Article 3.2.4.1?",null,null,null,null,null,null,"N/A"]
["Overall thermal Transmittance (m²K/W)"]
[null,null,null,null,null,"Proposed","NECB Limit "]
[null,null,null,null,null,null,"HDD @ 18","HDD @ 15"]
["Opaque walls (above ground) ",null,null,null,null,null,"≤ 0.215","≤ 0.240"]
["Opaque walls (in contact with ground) ",null,null,null,null,null,"≤ 0.284","≤ 0.284"]
["Roofs (above ground) ",null,null,null,null,null,"≤ 0.121","≤ 0.138"]
["Roofs (in contact with ground) ",null,null,null,null,null,"≤ 0.284","≤ 0.284"]
["Floors (above ground) ",null,null,null,null,null,"≤ 0.138","≤ 0.156"]
["Floors (in contact with ground)",null,null,null,null,null,"≤ 0.757 for 1.2m ","≤ 0.757 for 1.2m "]
["Vertical Fenestration",null,null,null,null,null,"≤ 1.73","≤ 1.73"]
["Skylights ",null,null,null,null,null,"≤ 2.41","≤ 2.41"]
["FWDR",null,null,null,null,null,{"$f":"\"≤ \"&ROUND((2000-0.2*5000)/3000,2)","v":"≤ 0.33"},{"$f":"\"≤ \"&ROUND((2000-0.2*4050)/3000,2)","v":"≤ 0.4"}]
["Air Leakage (L/(s∙m2))"]
["Air Leakage Compliance Path",null,null,null,null,"N/A"]
["Fixed fenestration and curtain walls ",null,null,null,null,null,"≤ 0.20"]
["Operable windows, skylights, and doors ",null,null,null,null,null,"≤ 0.50"]
["Overhead doors",null,null,null,null,null,"≤ 2.0"]
["Operable revolving and auto sliding doors  ",null,null,null,null,null,"≤ 5.0"]
["Trade-off Path Compliance"]
[null,null,null,null,"Proposed (Uip*Aip) ",null,"Reference (Uir*Air)"]
["Vertical (above ground portions)"]
["Horizontal (above ground portions)"]
["UipAip is less than or equal to UirAir in conformance with NECB Article 3.3.1.2",null,null,null,null,null,null,"N/A"]
["UipAip calculations provided on drawings or as appendix?",null,null,null,null,null,null,"N/A"]
["Part 4 - Lighting "]
["General"]
["All prescriptive requirements in Division B, Section 4.2 met? ",null,null,null,null,null,null,"N/A"]
["All Trade-off requirements in Division B, Section 4.3 met? ",null,null,null,null,null,null,"N/A"]
["Interior and exterior installed Lighting Power included on the drawings?",null,null,null,null,null,null,"N/A"]
["Interior and exterior lighting controls provided on drawings or as appendix?",null,null,null,null,null,null,"N/A"]
["Interior Lighting (Prescriptive Path)"]
["Proposed building IILP (Installed Interior Lighting Power) (kW) "]
["Interior Lighting Power Allowance Method: ",null,null,null,null,null,null,"N/A"]
["Building Area Method:","ILPA (kW)"]
[null,"Gross lighted area (m2)"]
[null,"Lighting power density (W/m2)"]
["Space-by-Space Method:","ILPA (kW)"]
["Detailed breakdown of spaces, floor area, associated lighting power densities (W/m2), and resulting ILPA provided on drawings or as appendix?",null,null,null,null,null,null,"N/A"]
["Interior Lighting (Trade-off Path)"]
["IILE - Installed Interior Light Energy (kW∙h/a) (Proposed)"]
["ILEA - Interior Lighting Energy Allowance (kW∙h/a) (Reference)"]
["IILE and ILEA calculations provided on drawings or as appendix?",null,null,null,null,null,null,"N/A"]
["Exterior Lighting (Trade-off and Prescriptive)"]
[null,"Installed Lighting (W)",null,"Specific/General Allowance ",null,"Portion of Basic Allowance",null,"Total Allowance (W)"]
["Specific Lighting (T4.2.3.1-C)",null,"≤ ",null,"+",null,"=",{"$f":"D63+F63","v":0}]
["General (T4.2.3.1-D)",null,"≤ ",null,"+",null,"=",0]
["Other (T4.2.3.1-E)",null,"≤ ",null,"+",null,"=",0]
["Total",{"$f":"SUM(B63:B65)","v":0},"≤ ",{"$f":"SUM(D63:D65)","v":0},"+",{"$f":"SUM(F63:F65)","v":0},"=",0]
["Basic Site Allowance Check",null,null,null,null,{"$f":"SUM(F63:F65)","v":0},"≤ ",{"$f":"_xludf.IFS(B67=0,0,B67=1,350,B67=2,400,B67=3,500,B67=4,900)","v":{"$error":"#NAME?"}}]
["Detailed breakdown of installed Lighting Power and controls provided on drawings or as appendix?",null,null,null,null,null,null,"N/A"]
["Part 5 - Heating, Ventilation, and Air-Conditioning Systems"]
["General "]
["All prescriptive requirements in Division B, Section 5.2 met? ",null,null,null,null,null,null,"N/A"]
[null,null,null,null,"Proposed ",null,"NECB Limit "]
[null,null,null,null,"Constant Volume","Variable Air Volume ","Constant Volume","Variable Air Volume "]
["Fan system power demand ",null,null,null,null,null,"≤ 1.6 W per L/s","≤ 2.65 W per L/s"]
["Commercial kitchen design ventilation rate",null,null,null,null,null,"           ≤ 1410 L/s"]
[null,null,null,null,null,null,"          DCV provided"]
["Ducts sealed, insulated, and protected in conformance with Subsection 5.2.2. Intakes and outlets conform with Subsection 5.2.4",null,null,null,null,null,null,"N/A"]
["Economizer system required in conformance with Articles 5.2.2.7. Air economizer has been designed to Article 5.2.2.8  or Article 5.2.2.9.",null,null,null,null,null,null,"N/A"]
["Insulation and protection of piping systems for HVAC systems in conformance with Subsection 5.2.5. ",null,null,null,null,null,null,"N/A"]
["Temperature controls been designed in conformance with Subsection 5.2.8. ",null,null,null,null,null,null,"N/A"]
["Type of ventilation system operation ",null,null,null,null,null,null,"N/A"]
["Percentage of outdoor air at design airflow conditions (%)"]
["Energy recovery system required ",null,null,null,null,null,null,"N/A"]
["Energy recovery system efficiency (%) "]
["Proposed HVAC Equipment"]
["Component or Equipment","Location or Identifier","Input ","Capacity","Flow","Standard","Rating Conditions","Rated Performance "]
["(include on mechanical drawings or as appendix)"]
[]
["Complete list of equipment, if not listed on mechanical drawings, is provided?",null,null,null,null,null,null,"N/A"]
["Part 6 – Service Water Systems "]
["General "]
["All prescriptive requirements in Division B, Section 6.2 met? ",null,null,null,null,null,null,"N/A"]
[null,null,null,null,"Proposed ",null,"NECB Limit "]
["Shower heads (L/min) ",null,null,null,null,null,"≤ 7.6 L/min"]
["Private Lavatories (L/min)",null,null,null,null,null,"≤ 5.7 L/min"]
["Public Lavatories (L/min)",null,null,null,null,null,"≤ 1.9 L/min"]
["Service water piping insulated in conformance with Subsection 6.2.3",null,null,null,null,null,null,"N/A"]
["Proposed Service Hot Water Heating Equipment"]
["Component or Equipment","Location or Identifier","Input ","Capacity (L)","Vt (L)","Standard ","Rating Conditions","Rated Performance "]
["(include on mechanical drawings or as appendix)"]
[]
["Complete list of equipment, if not listed on mechanical drawings, is provided?",null,null,null,null,null,null,"N/A"]
["Part 7 - Power Systems"]
["General "]
["All prescriptive requirements in Division B, Section 7.2 met? ",null,null,null,null,null,null,"N/A"]
[null,null,null,null,"Proposed ",null,"NECB Limit "]
["Load Carrying Capacity (kVa)",null,null,null,null,null,"       ≤ 250 kVa"]
[null,null,null,null,null,null,"       Monitoring System Provided"]
["Declaration of Coordinating NECB Design Professional"]
["Building energy prescriptive and/or trade-off compliance meets NECB 2020",null,null,null,null,null,null,"N/A"]
["Name:",null,null,null,"Date:"]
["(INSERT CONTACT INFORMATION HERE)",null,null,null,"(SIGNATURE and STAMP, if applicable)"]